## Notes
Memory map of the PLC containing the EMS / PPC
General comments
MB Address columns are in decimal notation
Mapping port: 502
Holding registers
"Big endian" order
Access: it refers to external devices access permission to EMS memory
WRITE: Both read and write functions are allowed
READ: Only read functions allowed
SF: Scale Factor (value = MB_value * 10SF)
Data types: WORD type represents 16 bits. UINT type represents 16 bits unsigned integers. INT type represents 16 bits signed integers. UDINT type represents 32 bits unsigned integers. DINT type represents 32 bits signed integers.
Variables box in blue, the address is free or reserved.

## Commands
Tag | MB Address | Access | Data type | Unit | SF | Description
General
Activity_Indicator | 0 | WRITE | WORD | - | - | Activity indicator of the client modbus (SCADA or other MB device), who control the EMS. This variable should increases at least one unit every second. Freezing could also mean the device (SCADA or other MB device) is not correctly communicating with the PLC.
EMS_control_Enable | 1 | WRITE | WORD | - | - | This parameter should always be 1 unless control from the PPC wants to be overriden. If EnableEMS=0, PPC is only reading and no MB write functions are used at all. 0 = setpoints are not sent and PIDs are reset; 1 = normal operation
Save_Default_Values | 2 | WRITE | WORD | - | - | Saves current control data as default values. 0 = No save 1 = Save. The PPC change the value to 0 when the save has been done.
Unassigned
Photovoltaic plant (PV)
Limitations
Smax_config | 10 | WRITE | DINT | kVA | -1 | PV Plant Maximum Apparent Power
Pmax_config | 12 | WRITE | DINT | kW | -1 | PV Plant Maximum Active Power
Pmin_config | 14 | WRITE | DINT | kW | -1 | PV Plant Minimum Active Power
Qexp_config | 16 | WRITE | DINT | kVAr | -1 | PV Plant Maximum Reactive Power
Qimp_config | 18 | WRITE | DINT | kVAr | -1 | PV Plant Minimum Reactive Power
Pavailable | 20 | WRITE | DINT | kW | -1 | Avilable Power. Availability according to modeling
Unassigned
Control
F_controlMode | 30 | WRITE | WORD | - | - | Activation of the frequency response (PvsF) 0 = Disabled 1 = LFSM 2 = FSM
P_controlMode | 31 | WRITE | WORD | - | - | Active Power control Mode: 0 = Manual: PspPV setpoint is directly executed to the inverters, without regulation. 1 = Load following. PspPV is executed with regulation in PoC. 2 = Combined control with BESS: PspPoc 3 = FSC (only applicable in hybrid plants with diesel generators) 4 = Self-consumption (only for specific ad-hoc projects)
Q_controlMode | 32 | WRITE | WORD | - | - | Reactive power control mode: 0 = Manual: QspPV setpoint is directly applied to each inverter without regulation 1 = Set Point Q : reactive power is regulated at the POC. 2 = PF Set Point: reactive power is regulated at the POC as a function of active power to maintain the power factor at the POC. 3 = Voltage regulation: reactive power is regulated at the POC as a funtion of voltage, following a droop slope. 4 = Combined control with BESS: QModePoc
Pramp_activation | 33 | WRITE | WORD | - | - | Active power up ramp activation. 1 = Enabled. 0 = Disabled.
Qramp_activation | 34 | WRITE | WORD | - | - | Reactive power up ramp regulation. 1 = Enabled. 0 = Disabled. Only applied in Qmode = 1
Stop_command | 35 | WRITE | WORD | - | - | PV start/stop setpoint (0/1): if StopActivationPv = 1 the plant is stopped (all inverters stopped).
P_command | 36 | WRITE | DINT | kW | -1 | Active power setpoint PspPV. Direct write in mode Manual (1) or Load following (2).
Q_command | 38 | WRITE | DINT | kVAr | -1 | Reactive power set-point QspPV for QModePv = 1
V_command | 40 | WRITE | UDINT | V | 0 | Voltage set-point VspPV for QModePv = 3
Pramp_command | 42 | WRITE | UDINT | kW/s | 0 | Active power up and down ramp value.
Qramp_command | 44 | WRITE | UDINT | kW/s | 0 | Reactive power up ramp value. Only applied in Qmode = 1
PF_Command | 46 | WRITE | INT | pu | -3 | Power Factor set-point PFspPV for QModePv = 2. Positive implies sign(P)=sign(Q)
F_command | 47 | WRITE | UINT | Hz | -3 | Frequency reference FspPV for frequency response. It's usually not changed. Default 50 Hz.
Vdroop_slope | 48 | WRITE | UINT | pu | -3 | Voltage droop slope (QvsV). Example: this register = 40 --> applied slope is 4% (0,04 pu)
Fdroop_slope | 49 | WRITE | UINT | pu | -3 | Frequency droop slope (PvsF). Example: this register = 50 --> applied slope is 5% (0,05 pu)
DeltaP_command | 50 | WRITE | UINT | pu | -3 | Active power reserve depending on available power (PavailablePV)
Unassigned
Energy Storage Systems (ESS)
Limitations
Smax_config_BESS | 60 | WRITE | DINT | kVA | -1 | BESS Plant Maximum Apparent Power
Pmax_config_BESS | 62 | WRITE | DINT | kW | -1 | BESS Plant Maximum Active Power
Pmin_config_BESS | 64 | WRITE | DINT | kW | -1 | BESS Plant Minimum Active Power
Qexp_config_BESS | 66 | WRITE | DINT | kVAr | -1 | BESS Plant Maximum Reactive Power (positive, export)
Qimp_config_BESS | 68 | WRITE | DINT | kVAr | -1 | BESS Plant Minimum Reactive Power (negative, import)
SOCmax_config | 70 | WRITE | WORD | % | -2 | Maximum State of Charge.
SOCmin_config | 71 | WRITE | WORD | % | -2 | Minimum State of Charge.
Unassigned
Control
F_controlMode_BESS | 80 | WRITE | WORD | - | - | Activation of the frequency response (PvsF) 0 = Disabled 1 = LFSM 2 = FSM
P_controlMode_BESS | 81 | WRITE | WORD | - | - | Active Power control Mode: 0 = Manual: PspEss setpoint is directly executed to the inverters, without regulation. 1 = Load following. PspEss is executed with regulation in PoC. 2 = Combined control with PV: PspPoc 3 = FSC (only applicable in hybrid plants with diesel generators) 4 = Self-consumption (only for specific ad-hoc projects)
Q_controlMode_BESS | 82 | WRITE | WORD | - | - | Reactive power control mode: 0 = Manual: QspEss setpoint is directly applied to each inverter without regulation 1 = Set Point Q : reactive power is regulated at the POC. 2 = PF Set Point: reactive power is regulated at the POC as a function of active power to maintain the power factor at the POC. 3 = Voltage regulation: reactive power is regulated at the POC as a funtion of voltage, following a droop slope. 4 = Combined control with PV: QModePoc
Pramp_activation_BESS | 83 | WRITE | WORD | - | - | Active power up ramp activation. 1 = Enabled. 0 = Disabled.
Qramp_activation_BESS | 84 | WRITE | WORD | - | - | Reactive power up ramp regulation. 1 = Enabled. 0 = Disabled. Only applied in Qmode = 1
Stop_command_BESS | 85 | WRITE | WORD | - | - | BESS start/stop setpoint (0/1): if StopActivationEss = 1 the plant is stopped (all inverters stopped).
P_command_BESS | 86 | WRITE | DINT | kW | -1 | Active power setpoint PspEss. Direct write in mode Manual (1) or Load following (2).
Q_command_BESS | 88 | WRITE | DINT | kVAr | -1 | Reactive power set-point QspEss for QModeEss = 1
V_command_BESS | 90 | WRITE | UDINT | V | 0 | Voltage set-point VspEss for QModeEss = 3
Pramp_command_BESS | 92 | WRITE | UDINT | kW/s | 0 | Active power up and down ramp value.
Qramp_command_BESS | 94 | WRITE | UDINT | kW/s | 0 | Reactive power up and down ramp value. Only applied in Qmode = 1
PF_command_BESS | 96 | WRITE | INT | pu | -3 | Power Factor set-point PFspEss for QModeEss = 2. Positive implies sign(P)=sign(Q)
F_command_BESS | 97 | WRITE | UINT | Hz | -3 | Frequency reference FspEss for frequency response. It's usuallt not changed. Default 50 Hz.
Vdroop_slope_BESS | 98 | WRITE | UINT | pu | -3 | Voltage droop slope (QvsV). Example: this register = 40 --> applied slope is 4% (0,04 pu)
Fdroop_slope_BESS | 99 | WRITE | UINT | pu | -3 | Frequency droop slope (PvsF). Example: this register = 50 --> applied slope is 5% (0,05 pu)
Point of Connection control (for combined control PV-BESS)
Control
Q_controlMode_PoC | 101 | WRITE | WORD | - | - | Reactive power control mode: 0 = Manual: QspPoc setpoint is directly applied to each inverter without regulation 1 = Set Point Q : reactive power is regulated at the POC. 2 = PF Set Point: reactive power is regulated at the POC as a function of active power to maintain the power factor at the POC. 3 = Voltage regulation: reactive power is regulated at the POC as a funtion of voltage, following a droop slope.
P_command_PoC | 102 | WRITE | DINT | kW | -1 | Applied active power setpoint. PspPoc
Q_command_PoC | 104 | WRITE | DINT | kVAr | -1 | Reactive power set-point for QModePoc = 1. QspPoc
V_command_PoC | 106 | WRITE | UDINT | V | 0 | Voltage set-point for QModePoc = 3. VspPoc
PF_command_PoC | 108 | WRITE | INT | pu | -3 | Power Factor set-point for QModePoc = 2. Positive implies sign(P)=sign(Q). PFspPoc
Vdroop_slope_PoC | 109 | WRITE | UINT | pu | -3 | Voltage droop slope (QvsV). Example: this register = 40 --> applied slope is 4% (0,04 pu)
Unassigned
Gensets
Control
MinimumLoadRatio | 120 | WRITE | UINT | pu | -3 | Minimum Load Ratio: Minimum allowable load on the generator, as a percentage of its rated capacity.
Unassigned

## Measurements
Tag | MB Address | Access | Data type | Unit | SF | Description
Photovoltaic plant (PV)
Availability
Pnom_available | 200 | READ | DINT | kW | -1 | Nominal Active Power feedback from all enabled inverters of the PV plant.
Pmax_available | 202 | READ | DINT | kW | -1 | Maximum Active Power feedback from all enabled inverters of the PV plant.
Pmin_available | 204 | READ | DINT | kW | -1 | Minimum Active Power feedback from all enabled inverters of the PV plant.
Qexp_available | 206 | READ | DINT | kVAr | -1 | Maximum Rective Power feedback from all enabled inverters of the PV plant.
Qimp_available | 208 | READ | DINT | kVAr | -1 | Minimum Reactive Power feedback from all enabled inverters of the PV plant.
Inv_available | 210 | READ | WORD | - | - | Number of enabled inverters. Sum of all active inverters that are available.
Unassigned
Measurements
P_measurement | 220 | READ | DINT | kW | -1 | Aggregated active power measurement of all PV inverters
Q_measurement | 222 | READ | DINT | kVAr | -1 | Aggregated reactive power measurement of all PV inverters
S_measurement | 224 | READ | UDINT | kVA | -1 | Aggregated aparent power measurement of all PV inverters. Calculated from the previous active and reactive powers.
V_measurement | 226 | READ | UDINT | V | 0 | Voltage measurement at inverter terminals (inverters connected and with alive communications).
PF_measurement | 228 | READ | INT | pu | -3 | Aggregated power factor measurement of all PV inverters. Calculated from the previous active and reactive powers.
F_measurement | 229 | READ | WORD | Hz | -3 | Frequency measurement at inverter terminals (inverters connected and with alive communications).
Inv_running | 230 | READ | WORD | - | - | 0 : No inverter enabled 1 : At least one inverter enabled
Unassigned
Energy Storage Systems (ESS)
Availability
Pnom_available_BESS | 240 | READ | DINT | kW | -1 | Nominal Active Power feedback from all enabled inverters of the BESS plant.
Pmax_available_BESS | 242 | READ | DINT | kW | -1 | Maximum Active Power feedback from all enabled inverters of the BESS plant.
Pmin_available_BESS | 244 | READ | DINT | kW | -1 | Minimum Active Power feedback from all enabled inverters of the BESS plant.
Qexp_available_BESS | 246 | READ | DINT | kVAr | -1 | Maximum Rective Power feedback from all enabled inverters of the BESS plant.
Qimp_available_BESS | 248 | READ | DINT | kVAr | -1 | Minimum Reactive Power feedback from all enabled inverters of the BESS plant.
Inv_available_BESS | 250 | READ | WORD | - | - | Number of enabled inverters. Sum of all active inverters that are available.
Bms_available | 251 | READ | WORD | - | - | Number of enabled BMS. Sum of all active BMS that are available.
Pchar_available | 252 | READ | UDINT | kW | -1 | Maximum available charging power of all enabled batteries
Pdischar_available | 254 | READ | UDINT | kW | -1 | Minimum availabledis charging power of all enabled batteries
Capacity_available | 256 | READ | UDINT | kWh | 0 | Energy available from all enabled batteries
CapacityChar_available | 258 | READ | UDINT | kWh | 0 | Charge energy available from all enabled batteries
CapacityDischar_available | 260 | READ | UDINT | kWh | 0 | Discharge energy available from all enabled batteries
Unassigned
Measurements
P_measurement_BESS | 270 | READ | DINT | kW | -1 | Aggregated active power measurement of all BESS inverters
Q_measurement_BESS | 272 | READ | DINT | kVAr | -1 | Aggregated reactive power measurement of all BESS inverters
S_measurement_BESS | 274 | READ | UDINT | kVA | -1 | Aggregated aparent power measurement of all BESS inverters. Calculated from the previous active and reactive powers.
V_measurement_BESS | 276 | READ | UDINT | V | 0 | Voltage measurement at inverter terminals (inverters connected and with alive communications).
PF_measurement_BESS | 278 | READ | INT | pu | -3 | Aggregated power factor measurement of all BESS inverters. Calculated from the previous active and reactive powers.
F_measurement_BESS | 279 | READ | WORD | Hz | -3 | Frequency measurement at inverter terminals (inverters connected and with alive communications).
Inv_running_BESS | 280 | READ | WORD | - | - | 0 : No inverter enabled 1 : At least one inverter enabled
SOC_measurement | 281 | WRITE | WORD | % | -2 | Average Soc of all enabled batteries
Unassigned
Point of Connection
Measurements
P_measurement_PoC | 290 | READ | DINT | kW | -1 | Total active power in PoC. Read from the power meter if comms are alilve, otherwise it's the addition of all inverters active power as directly measured from them. This applies for the followng Q, S measurements.
Q_measurement_PoC | 292 | READ | DINT | kVAr | -1 | Total reactive power in PoC
S_measurement_PoC | 294 | READ | UDINT | kVA | -1 | Total apparent power in PoC
V_measurement_PoC | 296 | READ | UDINT | V | 0 | Voltage of the grid in PoC
PF_measurement_PoC | 298 | READ | INT | pu | -3 | Total power factor in PoC
F_measurement_PoC | 299 | READ | WORD | Hz | -3 | Frequency of the grid in PoC
Gensets
Availability
Pnom_available_genset | 300 | READ | DINT | kW | -1 | Nominal Active Power feedback from all enabled gensets
Pmax_available_genset | 302 | READ | DINT | kW | -1 | Maximum Active Power feedback from all enabled gensets
Pmin_available_genset | 304 | READ | DINT | kW | -1 | Minimum Active Power feedback from all enabled gensets
Qexp_available_genset | 306 | READ | DINT | kVAr | -1 | Maximum Rective Power feedback from all enabled gensets
Qimp_available_genset | 308 | READ | DINT | kVAr | -1 | Minimum Reactive Power feedback from all enabled gensets
Genset_available | 310 | READ | WORD | - | - | Number of enabled gensets. Sum of all active gensets that are available.
Unassigned
Measurements
P_measurement_genset | 312 | READ | DINT | kW | -1 | Aggregated active power measurement of all gensets
Q_measurement_genset | 314 | READ | DINT | kVAr | -1 | Aggregated reactive power measurement of all gensets
S_measurement_genset | 316 | READ | UDINT | kVA | -1 | Aggregated aparent power measurement of all gensets. Calculated from the previous active and reactive powers.
V_measurement_genset | 318 | READ | UDINT | V | 0 | Voltage measurement at gensets terminals (gensets connected and with alive communications).
PF_measurement_genset | 320 | READ | INT | pu | -3 | Aggregated power factor measurement of all gensets. Calculated from the previous active and reactive powers.
F_measurement_genset | 321 | READ | WORD | Hz | -3 | Frequency measurement at gensets terminals (gensets connected and with alive communications).
Genset_running | 322 | READ | WORD | - | - | 0 : No gensets enabled 1 : At least one gensets enabled
Unassigned